## Slide 1: AES_Project_2021_2022
Politecnico di Milano
Automation and Control Engineering
Group’s Members:
Borgnino Michele
Crespi Davide Marco
Firetto Alessandro
Riva Alessandro

## Slide 2: Controlled system

## Slide 3: Heater model and tracking
Energy balance 
V: total volume of water in the network, nominal flow rate
Select experimentally a wc  (good tradeoff)

## Slide 4: Heater Temperature

## Slide 5: Pump model
Pump: 
Pipe Network : 
Flow rate assumed equal in the whole network  Assumption
EQUILIBRIUM
Compute the equilibrium point for n, by imposing = 

## Slide 6: Pump Model
Linearization
«Albegraic model»  Hydraulics dynamics much faster than temperature, can be neglected
(in reality: G with τ very small)
Use a PI =   dominant closed loop pole at 1/Ti
Design choices: Ta = 2500s  Ti = 500s (system settles quickly) K = 0,001 (to reduce oscillations)

## Slide 7: Pump Control

## Slide 8: Zones model

## Slide 9: Zones set point tracking

## Slide 12: Control signals of each actuator

## Slide 13: Power consumption

## Slide 14: Individual power consumptions

## Slide 15
Model with the implementation of Day-Night Control

## Slide 16
Components of the logic switching system:

## Slide 17
Temperature tracking of zone 1

## Slide 18
Temperature tracking of zone 2

## Slide 19
Zone 1 Temperature tracking with different low limits
Low limit= 5+273,15K
Low limit= 7+273,15K

## Slide 20: Power consumption with different outlet temperatures in day mode
If I change the reference outlet temperature of the heater I get the following power consumption diagrams,
where .

## Slide 21: Power consumption with different outlet pressure in day mode
The higher the reference pressure, the more the pump will be used. As the overall consumption remains the same, I can decrease or increase the pressure reference based on the efficiency of the heater and the pump.

## Slide 22: Comparison of different reference values in day mode
Modifying the pressure and outlet temperature references I don’t change the room temperature dynamics. I only have a small reduction of the amplitude of oscillations in the case I operate at higher pressure. It is not advisable therefore to operate at higher fluid temperatures because I don’t have consistent advantages.

## Slide 23: Power consumption with different outlet temperatures in day/night mode
The same behavior can also be observed in the day/night mode. The only difference with the previous case is that the same increment of the fluid temperature produces now a higher average power increase: 12% compared to a 10.7% increase in the day mode.

## Slide 24: Power consumption with different outlet pressure in day/night mode
As in the other case, higher pressure references mean more utilization of the pump instead of the heater. As during the night one of our objectives is to minimize the heater usage, we are more inclined to consider the second option.